## Summary
Riverbend Produce Limited
Coolstore 3 — Glycol Chilling Upgrade
Q900142 · Rev A
Built from | specification + preliminary P&ID
Lines | 54
Awaiting supplier / subcontractor price | 13
Engineer to enter | 30
Rules to confirm | 11
Cost
Margin | 0.15
Sell
Exchange rate assumed | NZ$1 = USD $0.58

## Schedule of prices
Ref | Description | Cost | Sell
7.1 | Compressor pack, including drives
7.2 | Evaporative condenser
7.3 | Chiller plate heat exchanger
7.4 | Glycol circulation — pumps, tanks and controls
7.5 | Unit coolers
7.6 | Glycol pipework, valves and insulation
7.7 | Installation labour, supervision and consumables
7.8 | Electrical power, control wiring and SCADA
7.9 | As-built documentation, training, O&M
7.10 | Commissioning, glycol charge and spares
7.11 | Twelve months defects liability and routine maintenance
Total (excl GST)

## Costing
Ref | Description | Code | Source | Who does it | Qty | Unit | Unit cost | Margin | Total | Note
7.1 | Compressor pack, including drives
| Compressor | C-COM | RFQ |  | 2 | ea |  | 15% |  | 90 kW each · IE5 VSD
7.2 | Evaporative condenser
| Condenser | C-CON | RFQ |  | 1 | ea |  | 15% |  | 620 kWR each · EC Fan Supply
7.3 | Chiller plate heat exchanger
| Chiller Phe | C-HX | RFQ |  | 1 | ea |  | 15% |  | 520 kWR each · no starter shown
7.4 | Glycol circulation — pumps, tanks and controls
| Glycol Pump | C-WP | RFQ |  | 2 | ea |  | 15% |  | 15 kW each · VSD
| Defrost Pump | C-WP | RFQ |  | 1 | ea |  | 15% |  | 4 kW each · VSD
7.5 | Unit coolers
| Unit Cooler | C-FCU | RFQ |  | 4 | ea |  | 15% |  | 55 kWR each · EC Fan Supply
7.6 | Glycol pipework, valves and insulation
| 50TE isolating valve | M-VG | RFQ |  | 10 | ea |  | 15% |  | 10 × 50TE on the P&ID
| 50TE tube flange | M-F | RULE |  | 10 | ea |  | 15% |  | rule: 1 per 50TE connection
| 50TE gasket | M-F | RULE |  | 10 | ea |  | 15% |  | rule: 1 per 50TE connection
| 80TE isolating valve | M-VG | RFQ |  | 6 | ea |  | 15% |  | 6 × 80TE on the P&ID
| 80TE tube flange | M-F | RULE |  | 6 | ea |  | 15% |  | rule: 1 per 80TE connection
| 80TE gasket | M-F | RULE |  | 6 | ea |  | 15% |  | rule: 1 per 80TE connection
| 40PN isolating valve | M-VG | RFQ |  | 2 | ea |  | 15% |  | 2 × 40PN on the P&ID
| 40PN gasket | M-F | RULE |  | 2 | ea |  | 15% |  | rule: 1 per 40PN connection
| 40PN bolt set | M-F | RULE |  | 2 | ea |  | 15% |  | rule: 1 per 40PN connection
| 65PN isolating valve | M-VG | RFQ |  | 1 | ea |  | 15% |  | 1 × 65PN on the P&ID
| 65PN gasket | M-F | RULE |  | 1 | ea |  | 15% |  | rule: 1 per 65PN connection
| 65PN bolt set | M-F | RULE |  | 1 | ea |  | 15% |  | rule: 1 per 65PN connection
| 65TE isolating valve | M-VG | RFQ |  | 1 | ea |  | 15% |  | 1 × 65TE on the P&ID
| 65TE tube flange | M-F | RULE |  | 1 | ea |  | 15% |  | rule: 1 per 65TE connection
| 65TE gasket | M-F | RULE |  | 1 | ea |  | 15% |  | rule: 1 per 65TE connection
| 42mm 304 press pipe | M-PFS | ENGINEER |  |  | m |  | 15% |  | 8 runs on the P&ID
| 100NB pipe | M-P | ENGINEER |  |  | m |  | 15% |  | 1 runs on the P&ID
| 80NB pipe | M-P | ENGINEER |  |  | m |  | 15% |  | 1 runs on the P&ID
| 101mm tube pipe | M-P | ENGINEER |  |  | m |  | 15% |  | 1 runs on the P&ID
| 63mm tube pipe | M-P | ENGINEER |  |  | m |  | 15% |  | 1 runs on the P&ID
| 76mm 304 press pipe | M-PFS | ENGINEER |  |  | m |  | 15% |  | 1 runs on the P&ID
| 54mm 304 press pipe | M-PFS | ENGINEER |  |  | m |  | 15% |  | 1 runs on the P&ID
| Pipe insulation | M-INS | RATE |  |  | m |  | 15% |  | rate card by diameter
| Freight and cartage | P-FRE | ENGINEER |  |  | lot |  | 15% |  | carried on past jobs
7.7 | Installation labour, supervision and consumables
| Set out and rig plant | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Pipe compressor pack | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Pipe chiller and glycol circuit | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Hang and pipe unit coolers | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Pressure test | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Insulate | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Glycol fill and flush | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Changeover weekend | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Supervision | L-SERVIN | ENGINEER | In-house |  | hr | 105 | 15% |  | crew × days
| Crane and access hire | P-HIRE | ENGINEER |  |  | lot |  | 15% |  | carried on past jobs
| Travel and accommodation | D-TRAV | ENGINEER |  |  | lot |  | 15% |  | carried on past jobs
| Site setup and safety | P-SS | ENGINEER |  |  | lot |  | 15% |  | carried on past jobs
7.8 | Electrical power, control wiring and SCADA
| Power and control wiring | ES-INST | RFQ | Subcontract | 1 | lot |  | 15% |  | from the maximum demand schedule
| SCADA integration — Ignition | ES-AU | RFQ | Subcontract | 1 | lot |  | 15% |  | electrical contractor
7.9 | As-built documentation, training, O&M
| As-built drawings | L-DWG | ENGINEER | In-house |  | hr | 140 | 15% |  | hours to be entered
| Training | L-DWG | ENGINEER | In-house |  | hr | 140 | 15% |  | hours to be entered
| O&M manuals | L-DWG | ENGINEER | In-house |  | hr | 140 | 15% |  | hours to be entered
| Producer statements | L-DV | ENGINEER | In-house |  | hr | 140 | 15% |  | hours to be entered
| Compliance and inspection | P-RCOMP | ENGINEER |  |  | lot |  | 15% |  | carried on past jobs
7.10 | Commissioning, glycol charge and spares
| Commissioning and pulldown demonstration | L-COM | ENGINEER | In-house |  | hr | 105 | 15% |  | to be entered
| Glycol charge — MPG 35% | R-GLY | ENGINEER |  |  | L |  | 15% |  | to be entered
| Spare parts | M-GEN | ENGINEER |  |  | ea |  | 15% |  | to be entered
7.11 | Twelve months defects liability and routine maintenance
| Routine maintenance, 12 months | D-MAINT | ENGINEER |  | 4 | visit |  | 15% |  | rate to be entered
| Contingency | D-CONT | ENGINEER |  |  | lot |  | 15% |  | carried on past jobs

## Electrical
Load | Duty | Unit | Starter | DI | DO | AI | RTD | AO | Comms | IFM
COMPRESSOR 1 | 90 | kW | IE5 VSD | 0 | 0 | 0 | 0 | 0 | 1 | 0
UNIT COOLER 1 | 55 | kWR | EC Fan Supply | 0 | 0 | 0 | 0 | 0 | 1 | 0
COMPRESSOR 2 | 90 | kW | IE5 VSD | 0 | 0 | 0 | 0 | 0 | 1 | 0
UNIT COOLER 2 | 55 | kWR | EC Fan Supply | 0 | 0 | 0 | 0 | 0 | 1 | 0
CONDENSER | 620 | kWR | EC Fan Supply | 0 | 0 | 0 | 0 | 0 | 1 | 0
UNIT COOLER 3 | 55 | kWR | EC Fan Supply | 0 | 0 | 0 | 0 | 0 | 1 | 0
CHILLER PHE | 520 | kWR | ENGINEER | ?? | ?? | ?? | ?? | ?? | ?? | ??
GLYCOL PUMP 1 | 15 | kW | VSD | 0 | 0 | 0 | 0 | 0 | 1 | 0
UNIT COOLER 4 | 55 | kWR | EC Fan Supply | 0 | 0 | 0 | 0 | 0 | 1 | 0
GLYCOL PUMP 2 | 15 | kW | VSD | 0 | 0 | 0 | 0 | 0 | 1 | 0
DEFROST PUMP | 4 | kW | VSD | 0 | 0 | 0 | 0 | 0 | 1 | 0
TOTAL CONNECTED | 1574 | kW |  | 0 | 0 | 0 | 0 | 0 | 10 | 0

## Take-off
From the P&ID | Size | Fitting | Count | Hours each | Total hours | Note
50TE | 2" | Buttweld | 10 |  |  | counted on the drawing
50TE | 2" | Elbow | 0 |  |  | counted on the drawing
80TE | 3" | Buttweld | 6 |  |  | counted on the drawing
80TE | 3" | Elbow | 0 |  |  | counted on the drawing
40PN | 1 1/2" | Buttweld | 2 |  |  | counted on the drawing
40PN | 1 1/2" | Elbow | 0 |  |  | counted on the drawing
65PN | 2 1/2" | Buttweld | 1 |  |  | counted on the drawing
65PN | 2 1/2" | Elbow | 0 |  |  | counted on the drawing
65TE | 2 1/2" | Buttweld | 1 |  |  | counted on the drawing
65TE | 2 1/2" | Elbow | 0 |  |  | counted on the drawing
42mm 304 press | 1 1/2" | Straight |  |  |  | metres ÷ 6 m stick → welds — enter metres
100NB | 4" | Straight |  |  |  | metres ÷ 6 m stick → welds — enter metres
80NB | 3" | Straight |  |  |  | metres ÷ 6 m stick → welds — enter metres
101mm tube | 4" | Straight |  |  |  | metres ÷ 6 m stick → welds — enter metres
63mm tube | 2 1/2" | Straight |  |  |  | metres ÷ 6 m stick → welds — enter metres
76mm 304 press | 3" | Straight |  |  |  | metres ÷ 6 m stick → welds — enter metres
54mm 304 press | 2" | Straight |  |  |  | metres ÷ 6 m stick → welds — enter metres
TOTAL

## Welding hours
Rates | Weld Neck | Slip On | Blind | Socket Weld | Straight | Buttweld | Elbow | Tee | Reducer | Cap | Branch | Stab In
1/2" | 0.7 | 0.7 | 0.23 | 0.3 | 0.25 | 0.5 | 1 | 1.5 | 0.9 | 0.5 | 0.75 | 0.45
3/4" | 0.98 | 0.98 | 0.32 | 0.42 | 0.35 | 0.7 | 1.4 | 2.1 | 1.26 | 0.7 | 1.05 | 0.63
1" | 1.26 | 1.26 | 0.41 | 0.54 | 0.45 | 0.9 | 1.8 | 2.7 | 1.62 | 0.9 | 1.35 | 0.81
1 1/4" | 1.54 | 1.54 | 0.5 | 0.66 | 0.55 | 1.1 | 2.2 | 3.3 | 1.98 | 1.1 | 1.65 | 0.99
1 1/2" | 1.89 | 1.89 | 0.61 | 0.81 | 0.68 | 1.35 | 2.7 | 4.05 | 2.43 | 1.35 | 2.03 | 1.22
2" | 2.38 | 2.38 | 0.77 | 1.02 | 0.85 | 1.7 | 3.4 | 5.1 | 3.06 | 1.7 | 2.55 | 1.53
2 1/2" | 2.8 | 2.8 | 0.9 | 1.2 | 1 | 2 | 4 | 6 | 3.6 | 2 | 3 | 1.8
3" | 3.08 | 3.08 | 0.99 | 1.32 | 1.1 | 2.2 | 4.4 | 6.6 | 3.96 | 2.2 | 3.3 | 1.98
4" | 3.78 | 3.78 | 1.22 | 1.62 | 1.35 | 2.7 | 5.4 | 8.1 | 4.86 | 2.7 | 4.05 | 2.43
5" | 4.34 | 4.34 | 1.4 | 1.86 | 1.55 | 3.1 | 6.2 | 9.3 | 5.58 | 3.1 | 4.65 | 2.79
6" | 4.9 | 4.9 | 1.57 | 2.1 | 1.75 | 3.5 | 7 | 10.5 | 6.3 | 3.5 | 5.25 | 3.15
8" | 6.3 | 6.3 | 2.02 | 2.7 | 2.25 | 4.5 | 9 | 13.5 | 8.1 | 4.5 | 6.75 | 4.05
hours to weld and fit one item, by pipe size — CoolLogic's own matrix, unchanged

## Rules
Applies to | Generates | Status
1 per TE connection | tube flange + gasket | confirm with engineers
1 per PN connection | gasket + bolt set | confirm with engineers
elbow | 2 × a butt weld of the same size | from their Labour Calculator
tee | 3 × a butt weld of the same size | from their Labour Calculator
straight pipe | 1 weld per 6 m stick | confirm with engineers
compressor | harmonic mitigation, packaged control, common return transducer | observed on past jobs
pump | anticondensation heaters, TT/FS switch, supply transducer | observed on past jobs
unit cooler | 2 × cold stop actuator, defrost inlet + outlet | observed on past jobs
condenser | fan speed control, water treatment interlock, basin heater | confirm with engineers
pipe insulation | $150 per metre by diameter | rate to be set with the sub
in-house vs subcontract | the code changes with it: L- own labour ↔ S- subcontract, E- own electrical ↔ ES- electrical sub | their own code families
VSD / IE5 VSD / EC Fan Supply | 1 comms point | observed on past jobs
Motor Starter DOL | 1 DI + 1 DO + 1 AO | observed on past jobs